## Cover Letter
Your Partners In Achieving Excellence
2026-04-13
| Our Ref: | 2603157RS
| Bid Stage: | Binding
| Bid Type: | Priced
| Revision | 01
M/S. PPPP Energy Limited
UUUUUUUUUUUU
UUUUUU India - 6666
| Kind Attn: | XXXXXX, Commercial Dept. XXXX@jsw.in, +91-1234 37449
| Subject: | Proposal For System Verification & Issue Resolutions at DDDDD Project Site
| Project: | 3 x CC MW DDDD Hydroelectric Project
Dear Sir,
With reference to various ongoing issues reported by you in the Vibration Monitoring System of Meggitt make reported vide your email dated 25 Jan 2026 & our subsequent email & telephonic conversations & our discussions today, we are pleased to submit our techno-commercial proposal for your perusal & approval. The proposal provides technical services & assistance for verification, rectification, monitoring and performance optimization of the Meggitt's VM600Mk2 Vibration Monitoring System and Air Gap Monitoring System installed on the Hydro Turbine Generator units. The services are intended to: • Identify Root Cause Of Current Issues Reported In the VMS & AGMS • Identify list of spares & consumables/items required to restore the system to normal operating performance levels • Final rectification of the issues as per the scope of works after installation of the spares etc. to be procured by JSW We trust that it aligns with your expectations of a comprehensive solution to resolve all reported issues and also addresses possible long term efficient usage of the installed systems. We request for your kind consideration to our enclosed offer & are open for you to provide us with any feedback that may help us improve our offering or serve you better. It is our endeavour to work very closely with an esteemed organization like yours and we look forward to a long & mutually rewarding relationship. Please let us know in case you need any other information or details.
Best Regards Ruthvik Satish Solutions Engineer ModAE India Private Limited
ModAE India Private Limited Regd. Office: 503C, Hiranandani Hill Crest, Hulimavu, Bangalore 560 076 CIN: U62099KA2024PTC185715 GST: 29AARCM8622J1ZQ |  |  | Tel: +91 70228 45329 email: ruthvik.satish@mod-ae.com

## SOW
Your Partners In Achieving Excellence
Scope of Services & Execution Plan for DDDD Site
Objective: The proposal provides technical services & assistance for verification, rectification, monitoring and performance optimization of the Meggitt's VM600Mk2 Vibration Monitoring System and Air Gap Monitoring System installed on the Hydro Turbine Generator units. The services are intended to: • Identify Root Cause Of Current Issues Reported In the VMS & AGMS
System Verification & Issue Resolutions Services: This phase addresses the immediate need to address all issues currently reported as per Issues List attached in the systems and may Include the following activities on as needed basis: Part-1: VM600Mk2 Rack & Hardware Verification • Verification of Meggitt VM600Mk2 Rack Health • Inspection of Installed Monitoring System Modules • Verification of Rack Loading & Slot Configuration • Inspection & Verification Of Sensors Functionality & Performance On As Needed Basis • Verification of Signal Loops & Sensor Outputs • Identification of possible sensor or signal conditioning issues such as ground loops, cable faults etc. • Verification & Validation of Alarm & Tripping Logics Part-2: VibroSight CMS Configuration & Performance Verification • Verification of VibroSight capture Configuration • Verification of CMS System Communication Interfaces • Verification of Database Storage, Historian Functionality & Backup Configuration • Verification of CMS Server Performance & Stability Part-3: Asset Surveillance Management Services (ASMS) • Analyze Static & Dynamic Data From Vibrosight CMS Software • Steady-State & Transient Data Analysis Of Overall Vibration Signals (Direct, 1X, 2X, nX), gap voltages etc. • Finetuning Of CMS Software For Machine Baseline Based On Industry Best Practices • Vibration Analysis & Identification Of Abnormal Machine Behaviour If Any
ModAE Deliverables • Identify root cause of current issues & identify list of spares/materials needed for resolutions • Resolution of ongoing issues after reciept of all required spares/materials • Periodic System verification and rectification reports during the AMC period • Vibration diagnostic assessment report on as needed basis Customer (JSW DDDD Site) Responsibilities • Access to the CMS server and monitoring system • Operational and maintenance history of machines • Ensure availability of all hardware, software licenses, spares & consumables required to restore the system & for effective maintance • Necessary shutdown windows for inspection activities • Safety permits and work clearances Exclusions: • Supply of sensors, modules incuding all spare parts, associated consumables etc. • Portable data acquisition services for machines not connected to the monitoring system • Major hardware replacement or software licensing • Any other service not explicitly mentioned or included in this proposal

## Issues List
Your Partners In Achieving Excellence
Sl. | Issue reported | Possible Causes | Proposed Resolution | Status | Additional Remarks
1 | The Vibration System CPU hangs very frequently and giving false tripping signal | 1. CPU faulty 2. HW errors persisting in event list 3. Loaded Rack i.e., all slots used | 1. Replace CPU or system reset/reboot 2. Trip relay will not be activated by CPU malfunction as MPS is independent of CPU malfunction. 3. Relay logic configuration verification to be carried out on VMS & SCADA 4. Limit load of the VM600 rack to <60% utilization | Open | CPU freezing not encountered during our site visits
2 | Data backup and Historian functionality are not in progress | 1. Vibrosight not setup for automatic backup 2. Insufficient Hard Disk Space 3. MPC4 card going into failsafe mode (Occurred twice since commissioning CMS system) | 1. Check system configuration/Backup 2. Additional Hard Disk Space or New Hard Disk of higher capacity to be added | Open | Problems may also be occurring due to unwarranted & force shutdown of the VibroSight Server as reported by PPPPP Personnel to our personnel during previous conversations. In few instances even MPC card licenses were missing/deleted.
3 | The server experiences frequent hanging and unexpected crashes | 1. Insufficient Hard Disk Space 2. Processor issues/capacity on server | 1. Additional Hard Disk Space or New Hard Disk of higher capacity to be added | Open | CMS Server has low disk space. Server configuration to be verified as per requirements for sufficient historical Data storage and software performance issues.
4 | During unit standstill conditions or during unit start-up after MIV opening, the unit’s trip on UCB Shaft X–Y axis vibration or TGB housing vibration | 1. Sensor Calibration 2. Machine Vibration Issue | 1. Check Sensor/Loop Healthiness check 2. Detailed Analysis of Vibration Signals (Diagnostics) to identify possible fault conditions in Machine | Open | Monitor Vibration Signals live trend during Run-up and Standby to identify high vibration signals. Sensor healthiness to be checked to eliminate machine trip due to EMI.
5 | In Unit #3,: a) One Air Gap sensor has not been working. b) One Air Gap sensor continuously shows alarm values | 1. Possible sensor/conditioner failure | 1. Sensor to be uninstalled and verified during shutdown 2. Replace sensor/conditioner if required | Open

## Proposal
Your Partners In Achieving Excellence
Proposal For System Verification & Issue Resolutions at DDDDD Project Site
Item-10 | System Verification & Issue Resolutions Services
Sl. | Item Category | Scope Of Work & Activities For Annual Maintenance Contract | Qty | Unit Price ₹ | Total Price ₹ | Unit Cost ₹ | Total Cost ₹
1 | Part-1: VM600Mk2 Rack & Hardware Verification | • Verification of Meggitt VM600Mk2 Rack Health • Inspection of Installed Monitoring System Modules • Verification of Rack Loading & Slot Configuration • Inspection & Verification Of Sensors Functionality & Performance On As Needed Basis • Verification of Signal Loops & Sensor Outputs • Identification of possible sensor or signal conditioning issues such as ground loops, cable faults etc. • Verification & Validation of Alarm & Tripping Logics | 1 |  | 0 |  | 0 | 0
2 | Part-2: VibroSight CMS Configuration & Performance Verification | • Verification of VibroSight capture Configuration • Verification of CMS System Communication Interfaces • Verification of Database Storage, Historian Functionality & Backup Configuration • Verification of CMS Server Performance & Stability | 1 |  | 0 |  | 0 | 0
3 | Part-3: Asset Surveillance Management Services (ASMS) | • Analyze Static & Dynamic Data From Vibrosight CMS Software • Steady-State & Transient Data Analysis Of Overall Vibration Signals (Direct, 1X, 2X, nX), gap voltages etc. • Finetuning Of CMS Software For Machine Baseline Based On Industry Best Practices • Vibration Analysis & Identification Of Abnormal Machine Behaviour If Any | 1 |  | 0 |  | 0 | 0
Total For | System Verification & Issue Resolutions Services |  |  | 0 |  | Total Cost ₹ | 0
Notes:
Maximum working hours shall not exceed 10 hours per day for safety compliance and shall be typically between 8Am & 8PM
Billing & Payment Milestones:
Milestone-1 | 40% Shall be billed & payable after preliminary inspection for identification of faults and based on the recommend spares if needed to be purchased by JSW |  |  |  |  | 0
Milestone-2 | 30% Shall be billed & payable after installation of spares, replacement items etc. & completion of final system verification |  |  |  |  | 0
Milestone-3 | 30% Shall be billed & payable after completion of all activities as per scope of work |  |  |  |  | 0